Section 23 09 23.11 – INSTRUMENTATION AND CONTROL FOR HVAC

  - CONTROL VALVES

- Threaded Globe Valves:

- Water system globe valves:

    - NPS 3/4 and Smaller, female NPT: brass body, stainless steel stem, brass trim and EPDM O-ring packing.

    - NPS 1 - 2, female NPT: bronze body, stainless steel stem, brass trim and EPDM O-ring packing.

    - Flow Characteristics:  2-Way Valves - Equal Percentage 3-Way Valves - A (Coil) = Equal Percentage, B (Bypass) = Linear.

    - Performance:

Media Temperature: 35℉ to 250 ℉ (2℃ to 120℃) for CG and 20℉ to 250 ℉ (-7℃ to 120℃) for DG.

Pressure:

Body: ANSI Class 250

Maximum Operating Differential: 25 psid (173 kPa) brass / 50 psid (345 kPa) Stainless steel trim

Close-off (valve and actuation assembly):  Refer to Close-off Charts (CG/DG 6)

Leakage IV (0.01% of Cv).

- Steam system globe valves:

    - NPS 3/4 and Smaller, female NPT: brass body, stainless steel stem, stainless steel trim and Teflon V-ring/EPDM O-ring packing.

    - NPS 1 – 2, female NPT: bronze body, stainless steel stem, stainless steel trim and Teflon V-ring/EPDM O-ring packing.

    - Flow Characteristics:  2-Way Valves - Equal Percentage 3-Way Valves - A (Coil) = Equal Percentage, B (Bypass) = Linear.

    - Performance:

- a.      Media Temperature: 35℉ to 250 ℉ (2℃ to 120℃) for CG and 20℉ to 337 ℉ (-7℃ to 170℃) for DG.

- b.        Pressure:

Body: ANSI Class 250

Maximum Operating Differential: 15 psid (103 kPa) stainless steel for CG / 50 psid (345 kPa) Stainless steel trim for DG

Close-off (valve and actuation assembly):  Refer to Close-off Charts (CG/DG 6)

            - Leakage IV (0.01% of Cv).

- Manufactured or distributed by Bray or equal.