Section 23 09 00 – INSTRUMENTATION AND CONTROL FOR HVAC

23 09 13 Instrumentation and Control Devices for HVAC

  - CONTROL VALVES

- Globe Valves:

- Water system globe valves:

    - NPS 2-1/2 and Larger:  ANSI 125 cast iron flanged body, stainless steel stem, bronze trim and EPDM O-ring packing.

    - Flow Characteristics:  Two-way valves shall have equal percentage characteristics; three-way valves shall have linear characteristics.

- Steam system globe valves:

    - NPS 2-1/2 and Larger:  ANSI 125 cast iron flanged body, stainless steel stem, stainless trim and EPDM O-ring packing.

    - Flow Characteristics:  Linear flow characteristics for both two and three way.

- Manufactured or distributed by Bray or equal.