Section 23 09 00 – INSTRUMENTATION AND CONTROL FOR HVAC

23 09 13 Instrumentation and Control Devices for HVAC

  - ACTUATORS

- Industrial Electric Actuators (ONLY TO BE USED WITH 13.33. E Butterfly Valves – Resilient Seat and 13.33. F Butterfly Valves – High Performance.)

  - The combination of valve and actuator shall meet the close-off requirements as specified in Section 2.16.D/E – Butterfly Valves.

  - Coupling: ISO 5211 mounting standards.

  - Overload Protection: 120VAC and 220VAC line voltage units shall have a built-in thermal overload protector with automatic reset.

  - Manual Override: Actuator shall be equipped with a declutchable hand wheel for manual operation.  Engagement of the manual hand wheel shall disconnect power to the motor.

  - Actuator shall have an option to provide remote indication of manual vs. automatic mode of operation.

  - Power Requirements:  24VAC, 120VAC or 220VAC

  - Auxiliary Switches:  Two SPDT rated 10A at 120 VAC or 10A at 220 VAC.

  - Temperature Rating: -20 to +150ºF.(-29 to +65ºC)

  - Housing:  Minimum requirement NEMA type 4X/ IP65 with polyester coating.  Actuator shall have an option for an internal heater to prevent condensation within the housing.  A visual indication beacon shall indicate position status of the device.

  - Agency Listing:  UL, CE, CSA

  - The manufacturer shall warrant for 18 months from shipment or one year from service date.

  - Bray S-70 or equal.